## Exported Data
Date | Company | AssetRef | AssetName | SupplySystemRef | SupplySystemName | Stage | HazardRef | HazardousEvent | PreLikelihood | PreConsequence | Risk | ControlMeasureName | ControlMeasureDetails | ControlMeasureGroup | PostLikelihood | PostConsequence | ResidualRisk | ParametersMonitored | ParameterSuiteCode | MonitoringRecords | OngoingValidationProcedures | Comments | DWICategory | AdditionalControlMeasureDetails | LegalInstrumentReference | HazardID
13 Oct 2017 | WSX | T33126200 | STURMINSTER MARSHALL/SHAPWICK TREATMENT WORKS | Y44000092;Y44000095;Y44000098 | ZONE 92 SHAPWICK;ZONE 95 LYTCHETT MATRAVERS;ZONE 98 CORFE MULLEN | Treatment | A002A | Turbidity >= 1 NTU at point of Disinfection | 3 | 3 | 9 |  | Ability to flush to waste; Auto shutdown; Disinfection policy; Procedures and training; Regular operation; Routine maintenance; Routine water quality sampling; Understanding location of water after shutdown; Water quality monitor data reviewed and appropriate process changes made |  | 2 | 3 | 6 | A002A;A002B |  |  |  | Sturminster Marshall - Disinfection::PRO | A |  |  | 98287A002AT33126200
13 Oct 2017 | WSX | T33126200 | STURMINSTER MARSHALL/SHAPWICK TREATMENT WORKS | Y44000092;Y44000095;Y44000098 | ZONE 92 SHAPWICK;ZONE 95 LYTCHETT MATRAVERS;ZONE 98 CORFE MULLEN | Treatment | A005 | Failure of gas room heating | 4 | 1 | 4 |  | Auto shutdown; Monitor / alarm systems; Routine maintenance; Visual inspections |  | 2 | 1 | 2 | A005 |  |  |  | Sturminster Marshall - Disinfection::PRO | A |  |  | 90560A005T33126200
13 Oct 2017 | WSX | T33126200 | STURMINSTER MARSHALL/SHAPWICK TREATMENT WORKS | Y44000092;Y44000095;Y44000098 | ZONE 92 SHAPWICK;ZONE 95 LYTCHETT MATRAVERS;ZONE 98 CORFE MULLEN | Treatment | C111A | Cryptosporidium in treated water | 2 | 5 | 10 |  | Ability to divert water to waste; Auto shutdown; Routine water quality sampling; Water quality monitor data reviewed and appropriate process changes made |  | 2 | 5 | 10 | C111A |  |  |  | Sturminster Marshall - Disinfection::PRO | A |  | WSX3421 | 98208C111AT33126200
13 Oct 2017 | WSX | T33126200 | STURMINSTER MARSHALL/SHAPWICK TREATMENT WORKS | Y44000092;Y44000095;Y44000098 | ZONE 92 SHAPWICK;ZONE 95 LYTCHETT MATRAVERS;ZONE 98 CORFE MULLEN | Treatment | F004 | Geological radioactivity release | 1 | 3 | 3 |  | Review literature and monitoring data |  | 1 | 3 | 3 | F004 |  |  |  | Sturminster Marshall - General::PRO | A |  |  | 102896F004T33126200
13 Oct 2017 | WSX | T33126200 | STURMINSTER MARSHALL/SHAPWICK TREATMENT WORKS | Y44000092;Y44000095;Y44000098 | ZONE 92 SHAPWICK;ZONE 95 LYTCHETT MATRAVERS;ZONE 98 CORFE MULLEN | Treatment | F005 | Geological radioactivity release | 1 | 3 | 3 |  | Review literature and monitoring data |  | 1 | 3 | 3 | F005 |  |  |  | Sturminster Marshall - General::PRO | A |  |  | 102896F005T33126200
13 Oct 2017 | WSX | T33126200 | STURMINSTER MARSHALL/SHAPWICK TREATMENT WORKS | Y44000092;Y44000095;Y44000098 | ZONE 92 SHAPWICK;ZONE 95 LYTCHETT MATRAVERS;ZONE 98 CORFE MULLEN | Treatment | F006 | Unpredicted increase due to human activity | 1 | 3 | 3 |  | Review literature and monitoring data |  | 1 | 3 | 3 | F006 |  |  |  | Sturminster Marshall - General::PRO | A |  |  | 102899F006T33126200
13 Oct 2017 | WSX | T33126200 | STURMINSTER MARSHALL/SHAPWICK TREATMENT WORKS | Y44000092;Y44000095;Y44000098 | ZONE 92 SHAPWICK;ZONE 95 LYTCHETT MATRAVERS;ZONE 98 CORFE MULLEN | Treatment | F007 | Geological radioactivity release | 1 | 3 | 3 |  | Review literature and monitoring data |  | 1 | 3 | 3 | F007 |  |  |  | Sturminster Marshall - General::PRO | A |  |  | 102896F007T33126200
13 Oct 2017 | WSX | T33126200 | STURMINSTER MARSHALL/SHAPWICK TREATMENT WORKS | Y44000092;Y44000095;Y44000098 | ZONE 92 SHAPWICK;ZONE 95 LYTCHETT MATRAVERS;ZONE 98 CORFE MULLEN | Treatment | F031 | Geological radioactivity release | 1 | 3 | 3 |  | Review literature and monitoring data |  | 1 | 3 | 3 | F031 |  |  |  | Sturminster Marshall - General::PRO | A |  |  | 102896F031T33126200
13 Oct 2017 | WSX | T33126200 | STURMINSTER MARSHALL/SHAPWICK TREATMENT WORKS | Y44000092;Y44000095;Y44000098 | ZONE 92 SHAPWICK;ZONE 95 LYTCHETT MATRAVERS;ZONE 98 CORFE MULLEN | Treatment | H033 | Equipment failure | 4 | 5 | 20 |  | Auto shutdown; Critical equipment backed up (duty / standby); Monitor / alarm systems; Procedures and training; Routine maintenance |  | 2 | 5 | 10 | C001;C002;C007;C009;C010;C013 |  |  |  | Sturminster Marshall - Disinfection::PRO | A |  |  | 90558H033T33126200
13 Oct 2017 | WSX | T33126200 | STURMINSTER MARSHALL/SHAPWICK TREATMENT WORKS | Y44000092;Y44000095;Y44000098 | ZONE 92 SHAPWICK;ZONE 95 LYTCHETT MATRAVERS;ZONE 98 CORFE MULLEN | Treatment | H033 | Failure of disinfection | 3 | 5 | 15 |  | Ability to divert water to waste; Auto shutdown; Automatic / manual / flow paced dose control; Automatic flow control; Critical equipment calibrated by operators; Critical equipment maintained by M&E team; Design criteria; Disinfection policy; Monitor / alarm systems; Routine maintenance |  | 1 | 5 | 5 | C001;C002;C007;C009;C010;C013 |  |  |  | Sturminster Marshall - Disinfection::PRO | A |  |  | 90559H033T33126200
13 Oct 2017 | WSX | T33126200 | STURMINSTER MARSHALL/SHAPWICK TREATMENT WORKS | Y44000092;Y44000095;Y44000098 | ZONE 92 SHAPWICK;ZONE 95 LYTCHETT MATRAVERS;ZONE 98 CORFE MULLEN | Treatment | H033 | Flow variation in contact tank / main | 3 | 5 | 15 |  | Auto shutdown; Disinfection policy; Monitor / alarm systems; Procedures and training |  | 1 | 5 | 5 | C001;C002;C007;C009;C010;C013 |  |  |  | Sturminster Marshall - Disinfection::PRO | A |  |  | 90562H033T33126200
13 Oct 2017 | WSX | T33126200 | STURMINSTER MARSHALL/SHAPWICK TREATMENT WORKS | Y44000092;Y44000095;Y44000098 | ZONE 92 SHAPWICK;ZONE 95 LYTCHETT MATRAVERS;ZONE 98 CORFE MULLEN | Treatment | H033 | Inadequate chlorine contact time | 4 | 5 | 20 |  | Auto shutdown; Automatic / manual / flow paced dose control; Contact arrangements; Disinfection policy; Super chlorination |  | 2 | 5 | 10 | C001;C002;C007;C009;C010;C013 |  |  |  | Sturminster Marshall - Disinfection::PRO | A |  |  | 90563H033T33126200
13 Oct 2017 | WSX | T33126200 | STURMINSTER MARSHALL/SHAPWICK TREATMENT WORKS | Y44000092;Y44000095;Y44000098 | ZONE 92 SHAPWICK;ZONE 95 LYTCHETT MATRAVERS;ZONE 98 CORFE MULLEN | Treatment | H041 | Chlorine gas leak | 4 | 1 | 4 |  | Auto shutdown; Chlor-guard in place; Chlorine detection equipment |  | 2 | 1 | 2 | H041 |  |  |  | Sturminster Marshall - Disinfection::PRO | A |  |  | 90554H041T33126200
13 Oct 2017 | WSX | T33126200 | STURMINSTER MARSHALL/SHAPWICK TREATMENT WORKS | Y44000092;Y44000095;Y44000098 | ZONE 92 SHAPWICK;ZONE 95 LYTCHETT MATRAVERS;ZONE 98 CORFE MULLEN | Treatment | H041 | Equipment failure | 4 | 1 | 4 |  | Auto shutdown; Critical equipment backed up (duty / standby); Monitor / alarm systems; Procedures and training; Routine maintenance |  | 2 | 1 | 2 | H041 |  |  |  | Sturminster Marshall - Disinfection::PRO | A |  |  | 90558H041T33126200
13 Oct 2017 | WSX | T33126200 | STURMINSTER MARSHALL/SHAPWICK TREATMENT WORKS | Y44000092;Y44000095;Y44000098 | ZONE 92 SHAPWICK;ZONE 95 LYTCHETT MATRAVERS;ZONE 98 CORFE MULLEN | Treatment | H041 | Failure of gas room heating | 4 | 1 | 4 |  | Auto shutdown; Monitor / alarm systems; Routine maintenance; Visual inspections |  | 2 | 1 | 2 | H041 |  |  |  | Sturminster Marshall - Disinfection::PRO | A |  |  | 90560H041T33126200
13 Oct 2017 | WSX | T33126200 | STURMINSTER MARSHALL/SHAPWICK TREATMENT WORKS | Y44000092;Y44000095;Y44000098 | ZONE 92 SHAPWICK;ZONE 95 LYTCHETT MATRAVERS;ZONE 98 CORFE MULLEN | Treatment | H041 | Loss of deployable output | 2 | 3 | 6 |  | Critical equipment maintained by M&E team; Routine maintenance |  | 1 | 3 | 3 | H041 |  |  |  | Sturminster Marshall - General::PRO | A |  |  | 97980H041T33126200
13 Oct 2017 | WSX | T33126200 | STURMINSTER MARSHALL/SHAPWICK TREATMENT WORKS | Y44000092;Y44000095;Y44000098 | ZONE 92 SHAPWICK;ZONE 95 LYTCHETT MATRAVERS;ZONE 98 CORFE MULLEN | Treatment | H041 | Running out of chemical supply | 1 | 1 | 1 |  | Auto shutdown; Monitor / alarm systems; Procurement procedures |  | 1 | 1 | 1 | H041 |  |  |  | Sturminster Marshall - Disinfection::PRO | A |  |  | 90565H041T33126200
13 Oct 2017 | WSX | T33126200 | STURMINSTER MARSHALL/SHAPWICK TREATMENT WORKS | Y44000092;Y44000095;Y44000098 | ZONE 92 SHAPWICK;ZONE 95 LYTCHETT MATRAVERS;ZONE 98 CORFE MULLEN | Treatment | H062 | Contamination - Unsealed hatches/covers | 1 | 5 | 5 |  | Design criteria; Routine maintenance; Sealed structures; Visual inspections |  | 1 | 5 | 5 | H062 |  |  |  | Sturminster Marshall - General::PRO | A |  |  | 103133H062T33126200
13 Oct 2017 | WSX | T33126200 | STURMINSTER MARSHALL/SHAPWICK TREATMENT WORKS | Y44000092;Y44000095;Y44000098 | ZONE 92 SHAPWICK;ZONE 95 LYTCHETT MATRAVERS;ZONE 98 CORFE MULLEN | Treatment | H062 | Contamination from using wrong chemical | 1 | 5 | 5 |  | Auto shutdown; Monitor / alarm systems; Procedures and training |  | 1 | 5 | 5 | A001;A002 |  |  |  | Sturminster Marshall - Disinfection::PRO | A |  |  | 90556H062T33126200
20 Nov 2017 | WSX | T33126200 | STURMINSTER MARSHALL/SHAPWICK TREATMENT WORKS | Y44000092;Y44000095;Y44000098 | ZONE 92 SHAPWICK;ZONE 95 LYTCHETT MATRAVERS;ZONE 98 CORFE MULLEN | Treatment | A002A | Turbidty on start up from all boreholes | 3 | 3 | 9 |  | Ability to flush to waste; Auto shutdown; Routine water quality sampling; Water quality monitor data reviewed and appropriate process changes made |  | 1 | 3 | 3 | A002A |  |  |  | Sturminster Marshall - General::PRO | A |  |  | 96093A002AT33126200
20 Nov 2017 | WSX | T33126200 | STURMINSTER MARSHALL/SHAPWICK TREATMENT WORKS | Y44000092;Y44000095;Y44000098 | ZONE 92 SHAPWICK;ZONE 95 LYTCHETT MATRAVERS;ZONE 98 CORFE MULLEN | Treatment | A012 | Nitrate carry over from catchment | 5 | 3 | 15 |  | Auto shutdown; Monitor / alarm systems; Monitors calibrated; Provision of additional treatment; Water quality monitor data reviewed and appropriate process changes made |  | 5 | 3 | 15 | A012 |  |  |  | Sturminster Marshall - General::PRO | E | Integrated network grid to control nitrate levels:: | WSX2892 | 91589A012T33126200
20 Nov 2017 | WSX | T33126200 | STURMINSTER MARSHALL/SHAPWICK TREATMENT WORKS | Y44000092;Y44000095;Y44000098 | ZONE 92 SHAPWICK;ZONE 95 LYTCHETT MATRAVERS;ZONE 98 CORFE MULLEN | Treatment | A012 | Nitrate carry over from catchment | 5 | 3 | 15 |  | Auto shutdown; Water quality monitor data reviewed and appropriate process changes made |  | 5 | 3 | 15 | A012 |  |  |  | Sturminster Marshall - Disinfection::PRO | E | Investigate options for future nitrate risks::Investigate options to mitigate future nitrate risks |  | 108004A012T33126200