## Exported Data
Date | Company | AssetRef | AssetName | SupplySystemRef | SupplySystemName | Stage | HazardRef | HazardousEvent | PreLikelihood | PreConsequence | Risk | ControlMeasureName | ControlMeasureDetails | ControlMeasureGroup | PostLikelihood | PostConsequence | ResidualRisk | ParametersMonitored | ParameterSuiteCode | MonitoringRecords | OngoingValidationProcedures | Comments | DWICategory | AdditionalControlMeasureDetails | LegalInstrumentReference | HazardID
04 Aug 2016 | WSX | T33081000 | FONTHILL BISHOP TREATMENT WORKS | Y44000101 | ZONE 101 SHAFTESBURY | Treatment | H033 | Incorrect dose of chemical | 3 | 5 | 15 |  | Auto shutdown; Automatic / manual / flow paced dose control; Critical equipment backed up (duty / standby); Monitor / alarm systems |  | 2 | 5 | 10 | C001;C002;C007;C009;C010;C013 |  |  |  | Fonthill Bishop - Disinfection::PRO | A | Upgrade the CL2 dosing equipment::Improve the cl2 dosing equipment and control not up to standard. Dosing lines need to be double contained and splash guard required. |  | 89899H033T33081000
04 Aug 2016 | WSX | T33081000 | FONTHILL BISHOP TREATMENT WORKS | Y44000101 | ZONE 101 SHAFTESBURY | Treatment | P006 | Presence of pesticides | 4 | 2 | 8 |  | Catchment Management; Routine water quality sampling; Variable / fixed speed pumps |  | 4 | 2 | 8 | P006 |  |  |  | Fonthill Bishop - General::PRO | A | Install Permanent Borehole Washouts:: Integrated network grid to control nitrate levels:: | WSX2892 | 96055P006T33081000
06 Oct 2016 | WSX | T33081000 | FONTHILL BISHOP TREATMENT WORKS | Y44000101 | ZONE 101 SHAFTESBURY | Treatment | F006 | Unpredicted increase due to human activity | 1 | 3 | 3 |  | Review literature and monitoring data |  | 1 | 3 | 3 | F006 |  |  |  | Fonthill Bishop - General::PRO | A |  |  | 102854F006T33081000
09 Feb 2015 | WSX | T33081000 | FONTHILL BISHOP TREATMENT WORKS | Y44000101 | ZONE 101 SHAFTESBURY | Treatment | H033 | Incorrect softened water used to make sodium hypochlorite | 4 | 5 | 20 |  | Routine maintenance; Visual inspections |  | 2 | 5 | 10 | C001;C002;C007;C009;C010;C013 |  |  |  | Fonthill Bishop - Disinfection::PRO | A |  |  | 89901H033T33081000
09 Feb 2015 | WSX | T33081000 | FONTHILL BISHOP TREATMENT WORKS | Y44000101 | ZONE 101 SHAFTESBURY | Treatment | H033 | Running out of chemical supply | 4 | 5 | 20 |  | Auto shutdown; Monitor / alarm systems |  | 2 | 5 | 10 | C001;C002;C007;C009;C010;C013 |  |  |  | Fonthill Bishop - Disinfection::PRO | A |  |  | 89902H033T33081000
10 Nov 2016 | WSX | T33081000 | FONTHILL BISHOP TREATMENT WORKS | Y44000101 | ZONE 101 SHAFTESBURY | Treatment | H062 | Contamination - Unsealed hatches/covers | 1 | 5 | 5 |  | Design criteria; Routine maintenance; Sealed structures; Visual inspections |  | 1 | 5 | 5 | H062 |  |  |  | Fonthill Bishop - General::PRO | A |  |  | 103106H062T33081000
11 Oct 2016 | WSX | T33081000 | FONTHILL BISHOP TREATMENT WORKS | Y44000101 | ZONE 101 SHAFTESBURY | Treatment | F004 | Geological radioactivity release | 1 | 3 | 3 |  | Review literature and monitoring data |  | 1 | 3 | 3 | F004 |  |  |  | Fonthill Bishop - General::PRO | A |  |  | 102777F004T33081000
11 Oct 2016 | WSX | T33081000 | FONTHILL BISHOP TREATMENT WORKS | Y44000101 | ZONE 101 SHAFTESBURY | Treatment | F005 | Geological radioactivity release | 1 | 3 | 3 |  | Review literature and monitoring data |  | 1 | 3 | 3 | F005 |  |  |  | Fonthill Bishop - General::PRO | A |  |  | 102777F005T33081000
11 Oct 2016 | WSX | T33081000 | FONTHILL BISHOP TREATMENT WORKS | Y44000101 | ZONE 101 SHAFTESBURY | Treatment | F007 | Geological radioactivity release | 1 | 3 | 3 |  | Review literature and monitoring data |  | 1 | 3 | 3 | F007 |  |  |  | Fonthill Bishop - General::PRO | A |  |  | 102777F007T33081000
11 Oct 2016 | WSX | T33081000 | FONTHILL BISHOP TREATMENT WORKS | Y44000101 | ZONE 101 SHAFTESBURY | Treatment | F031 | Geological radioactivity release | 1 | 3 | 3 |  | Review literature and monitoring data |  | 1 | 3 | 3 | F031 |  |  |  | Fonthill Bishop - General::PRO | A |  |  | 102777F031T33081000
12 Oct 2015 | WSX | T33081000 | FONTHILL BISHOP TREATMENT WORKS | Y44000101 | ZONE 101 SHAFTESBURY | Treatment | H033 | Flow meter out of calibration or signal failure | 4 | 5 | 20 |  | Auto shutdown; Auto trim will rectify; Monitor / alarm systems; Routine maintenance |  | 2 | 5 | 10 | C001;C002;C007;C009;C010;C013 |  |  |  | Fonthill Bishop - Disinfection::PRO | A |  |  | 89897H033T33081000
12 Oct 2015 | WSX | T33081000 | FONTHILL BISHOP TREATMENT WORKS | Y44000101 | ZONE 101 SHAFTESBURY | Treatment | H033 | Inadequate chlorine contact time | 2 | 5 | 10 |  | Auto shutdown; Automatic / manual / flow paced dose control; Contact arrangements; Disinfection policy; Super chlorination |  | 1 | 5 | 5 | C001;C002;C007;C009;C010;C013 |  |  |  | Fonthill Bishop - Disinfection::PRO | A |  |  | 89898H033T33081000
12 Oct 2015 | WSX | T33081000 | FONTHILL BISHOP TREATMENT WORKS | Y44000101 | ZONE 101 SHAFTESBURY | Treatment | H033 | Process Contamination | 2 | 5 | 10 |  | Sealed structures; Security / integrity of motive water |  | 1 | 5 | 5 | C001;C002;C007;C009;C010;C013 |  |  |  | Fonthill Bishop - Disinfection::PRO | A |  |  | 89893H033T33081000
12 Oct 2015 | WSX | T33081000 | FONTHILL BISHOP TREATMENT WORKS | Y44000101 | ZONE 101 SHAFTESBURY | Treatment | H062 | Contamination from using wrong chemical | 2 | 5 | 10 |  | Auto shutdown; Monitor / alarm systems; Procedures and training |  | 1 | 5 | 5 | A001;A002 |  |  |  | Fonthill Bishop - Disinfection::PRO | A |  |  | 89892H062T33081000
12 Oct 2015 | WSX | T33081000 | FONTHILL BISHOP TREATMENT WORKS | Y44000101 | ZONE 101 SHAFTESBURY | Treatment | H062 | Flow meter out of calibration or signal failure | 4 | 5 | 20 |  | Auto shutdown; Auto trim will rectify; Monitor / alarm systems; Routine maintenance |  | 2 | 5 | 10 | A001;A002 |  |  |  | Fonthill Bishop - Disinfection::PRO | A |  |  | 89897H062T33081000
12 Oct 2015 | WSX | T33081000 | FONTHILL BISHOP TREATMENT WORKS | Y44000101 | ZONE 101 SHAFTESBURY | Treatment | H062 | Process Contamination | 2 | 5 | 10 |  | Sealed structures; Security / integrity of motive water |  | 1 | 5 | 5 | A001;A002 |  |  |  | Fonthill Bishop - Disinfection::PRO | A |  |  | 89893H062T33081000
18 Jul 2016 | WSX | T33081000 | FONTHILL BISHOP TREATMENT WORKS | Y44000101 | ZONE 101 SHAFTESBURY | Treatment | A002A | Turbidity >= 1 NTU at point of Disinfection | 5 | 2 | 10 |  | Ability to flush to waste; Auto shutdown; Disinfection policy; Procedures and training; Regular operation; Routine maintenance; Routine water quality sampling; Understanding location of water after shutdown; Water quality monitor data reviewed and appropr |  | 4 | 2 | 8 | A002A;A002B |  |  |  | Fonthill Bishop - Disinfection::PRO | A | Upgrade the CL2 dosing equipment::Improve the cl2 dosing equipment and control not up to standard. Dosing lines need to be double contained and splash guard required. |  | 98258A002AT33081000
18 Jul 2016 | WSX | T33081000 | FONTHILL BISHOP TREATMENT WORKS | Y44000101 | ZONE 101 SHAFTESBURY | Treatment | H033 | Equipment failure | 3 | 5 | 15 |  | Auto shutdown; Critical equipment backed up (duty / standby); Monitor / alarm systems; Procedures and training; Routine maintenance |  | 2 | 5 | 10 | C001;C002;C007;C009;C010;C013 |  |  |  | Fonthill Bishop - Disinfection::PRO | A | NRV in to installed on Littledown Main:: |  | 89895H033T33081000
18 Jul 2016 | WSX | T33081000 | FONTHILL BISHOP TREATMENT WORKS | Y44000101 | ZONE 101 SHAFTESBURY | Treatment | H033 | Failure of disinfection | 4 | 5 | 20 |  | Auto shutdown; Critical equipment calibrated by operators; Critical equipment maintained by M&E team; Monitor / alarm systems |  | 2 | 5 | 10 | C001;C002;C007;C009;C010;C013 |  |  |  | Fonthill Bishop - Disinfection::PRO | A | Upgrade the CL2 dosing equipment::Improve the cl2 dosing equipment and control not up to standard. Dosing lines need to be double contained and splash guard required. |  | 89896H033T33081000
18 Jul 2016 | WSX | T33081000 | FONTHILL BISHOP TREATMENT WORKS | Y44000101 | ZONE 101 SHAFTESBURY | Treatment | H033 | Turbidity >= 1 NTU at point of Disinfection | 5 | 3 | 15 |  | Ability to flush to waste; Auto shutdown; Disinfection policy; Procedures and training; Regular operation; Routine maintenance; Routine water quality sampling; Understanding location of water after shutdown; Water quality monitor data reviewed and appropr |  | 4 | 3 | 12 | H033 |  |  |  | Fonthill Bishop - Disinfection::PRO | A | Upgrade the CL2 dosing equipment::Improve the cl2 dosing equipment and control not up to standard. Dosing lines need to be double contained and splash guard required. |  | 98258H033T33081000
18 Jul 2016 | WSX | T33081000 | FONTHILL BISHOP TREATMENT WORKS | Y44000101 | ZONE 101 SHAFTESBURY | Treatment | H062 | Equipment failure | 3 | 5 | 15 |  | Auto shutdown; Critical equipment backed up (duty / standby); Monitor / alarm systems; Procedures and training; Routine maintenance |  | 2 | 5 | 10 | A001;A002 |  |  |  | Fonthill Bishop - Disinfection::PRO | A | NRV in to installed on Littledown Main:: |  | 89895H062T33081000
18 Jul 2016 | WSX | T33081000 | FONTHILL BISHOP TREATMENT WORKS | Y44000101 | ZONE 101 SHAFTESBURY | Treatment | H062 | Turbidity >= 1 NTU at point of Disinfection | 5 | 3 | 15 |  | Ability to flush to waste; Auto shutdown; Disinfection policy; Procedures and training; Regular operation; Routine maintenance; Routine water quality sampling; Understanding location of water after shutdown; Water quality monitor data reviewed and appropr |  | 4 | 3 | 12 | H062 |  |  |  | Fonthill Bishop - Disinfection::PRO | A | Upgrade the CL2 dosing equipment::Improve the cl2 dosing equipment and control not up to standard. Dosing lines need to be double contained and splash guard required. |  | 98258H062T33081000
29 Nov 2017 | WSX | T33081000 | FONTHILL BISHOP TREATMENT WORKS | Y44000101 | ZONE 101 SHAFTESBURY | Treatment | A012 | Nitrate carry over from catchment | 5 | 3 | 15 |  | Auto shutdown; Water quality monitor data reviewed and appropriate process changes made |  | 5 | 3 | 15 | A012 |  |  |  | Fonthill Bishop - Disinfection::PRO | E |  |  | 108008A012T33081000
29 Nov 2017 | WSX | T33081000 | FONTHILL BISHOP TREATMENT WORKS | Y44000101 | ZONE 101 SHAFTESBURY | Treatment | A012 | Nitrate carry over from catchment | 5 | 3 | 15 |  | Refer to Catchment WPP; Temporary Nitrate Blending Facility; Water quality monitor data reviewed and appropriate process changes made |  | 5 | 3 | 15 | A012 |  |  |  | Fonthill Bishop - General::PRO | E | Additional nitrate monitors required:: Install Permanent Borehole Washouts:: Integrated network grid to control nitrate levels:: | WSX2892 | 91587A012T33081000